ANNEXURE I

TECHNICAL SPECIFICATIONS FOR 50 W WHITE-LED BASED SOLAR STREET LIGHTING SYSTEM

| Sr. No | Components | Specification for Solar street light fitting |
| --- | --- | --- |
| 1 | PV module | 125 Wp under STC |
| 2 | Battery | Minimum 12.8V, 48 AH capacity Lithium Ferro Phosphate battery. |
| 3 | Light Source | White Light Emitting Diode (W-LED) 50 Watt, W-LED luminaire, dispersed beam, soothing to eyes with the use of proper optics and diffuser. Test report for same should be submitted. (LED + Driver) DC operated confirming to IP65 or above with proper dimmer arrangement Using LEDs which emits ultraviolet light will not be Permitted |
| 4 | Light Out put | The luminaire must use high efficacy W-LED with minimum 140 lumens per watt (and UV free). [A certificate to be submitted by the System supplier to the Test Lab during certification] |
| 5 | Mounting of light | Luminaire shall be at 6 m above the ground level & mounted properly. Foundation should be properly done to ensure safety. |
| 6 | Electronics Efficiency | Overall total Efficiency of the Electronics should be Minimum 90% |
| 7 | Duty Cycle | Dusk to dawn: First 6 Hours full light (Min. 24 Lux), rest of the time at lower light (50%, Min. 12 Lux) level. (Higher light output will be preferred) |
| 8 | Autonomy | 3 days or Minimum 36 operating hours per permissible discharge with fully charged Lithium-Ferro Phosphate Battery. |
| 9 | Ingress Protection – IP | Optical and Control gear compartment - IP 65 / IP 66 |
| 10 | Pole | 6 mtr long Octagonal hot dip galvanized Pole of 3 mm thickness having base plate arrangement to fix with nut & bolt on concrete platform. |
| 11 | Civil Work | As shown in diagram |

TECHNICAL DETAILS:

PV MODULE:

- Indigenously manufactured PV module should be used.

- The PV module should have crystalline silicon solar cells and must have a certificate of testing  conforming  to  IEC  61215  Edition  II  /  BIS  14286  from  an  NABL  or  IECQ accredited Laboratory.

- The power output of the module under STC should be a minimum of 125Wp.

- The module efficiency should not be less than 14 %.

- The terminal box on the module should have a provision for opening it for replacing the cable, if required.

- There should be a Name Plate fixed inside the module which will give:

- Name of the Manufacturer or Distinctive Logo.

- Model Number

- Serial Number

- Year of manufacture

- A  distinctive  serial  number  starting  with  NSM  will  be  engraved  on  the  frame  of  the module or screen printed on the tedlar sheet of the module.

BATTERY

- Minimum 12.8V, 48 AH capacity Lithium Ferro Phosphate Battery.

- Battery pack should have proper ‘Battery management System’ (BMS) for cell balancing, over charge and over temperature protection.

- Battery should conform to the latest BIS/ International standards.

LIGHT SOURCE

- The light source will be a white LED type.

- W-LEDs should not emit ultraviolet light.

- The  light output  from  the  white  LED  light  source  should  be constant  throughout the duty cycle.

- The lamps should be housed in an assembly suitable for outdoor use.

- The temperature  of  heat  sink  should  not  increase  more  than  20℃  above  ambient temperature during the dusk to dawn operation.

ELECTRONICS

- The total electronic efficiency should be at least 90 %.

- Charge controller should be MPPT Type.

- Electronics should operate at an appropriate voltage suitable for proper charging of the battery.

- The PV module itself should be used to sense the ambient light level for switching ON and OFF the lamp.

- The  PCB  containing  the  electronics  should  be  capable  of  solder  free  installation  and replacement.

- Necessary  lengths  of  wires/cables,  switches  suitable  for  DC  use  and fuses  should  be provided.

ELECTRONIC PROTECTIONS

- Adequate  protection  is  to  be  incorporated  under  “No  Load”  conditions  e.g. when the lamp is removed and the system is switched ‘ON’.

- The  system  should  have  protection  against  battery  overcharge  and  deep  discharge conditions.

- The System should have protection against short circuit conditions.

- Protection for reverse flow of current through the PV module(s) should be provided.

- Adequate protection should be provided against battery reverse polarity.

- Load reconnect should be provided at 80% of the battery capacity status.

MECHANICAL COMPONENTS

- Pole should be Hot dip galvanized pipe as per IS1161 & IS4736 i.e. Class B.

- Pole height 6 m above the ground level. Luminaire shall be at 6 m above the ground level & fixed properly in foundation to ensure safety.

- The pole should have the provision to hold the luminaire.

- The battery shall be included in the luminaire enclosure, which should be water proof (IP 65) and corrosion resistant.

INDICATORS

- The system should have two indicators, green and red.

- The  green  indicator should  indicate the charging under  progress  and  should  glow only when  the  charging  is  taking  place.   It should stop glowing when the battery is fully charged.

- Red indicator should indicate the battery “Load Cut Off” condition.

QUALITY AND WARRANTY

- The street lighting system (including the battery) will be warranted for a period of five years from the date of supply.

- The PV module(s) will be warranted for a minimum period of 25 years from the date of supply. The  PV  modules  must  be  warranted  for  their  output  peak  watt  capacity,  which should not be less than 90% at the end of Ten (10) years and 80% at the end of Twenty five (25) years.

- The Warranty Card to be supplied with the system must contain the details of the system.

OPERATION and MAINTENANCE MANUAL

An Operation, Instruction and Maintenance Manual, in English and marathi, should be provided with the Solar Street Lighting System. The following minimum details must be provided in the Manual:

- A  small  write-up  (with  a  block  diagram)  on  Solar  Street  Lighting  System  -  its components,   PV   module,   battery,   electronics   and   luminaire   and   expected performance.

- Type, Model number, Voltage & capacity of the battery, used in the system.

- About Charging and Significance of indicators.

- Clear instructions about erection of pole and mounting of PV module (s) and lamp housing assembly on the pole.

- Clear instructions on regular maintenance and troubleshooting of the Solar Street Lighting System.

- DO's and DONT's.

- Name  and  address  of  the  contact  person  for  repair  and  maintenance,  in  case  of non-functionality of the solar street lighting system.